## Slide 1: NETWORK OPERATION WITH THE INTRODUCTION OF NEW TECHNOLOGIES IN THE ELECTRICITY MARKET WITH FOCUS ON ENERGY STORAGE
Dinos Charalambides
Electrical Engineer

## Slide 2: Outline
Brief description of the network
System operating challenges due to,
    RES
    Opening of the Market
    Market Rules
Use of Energy Storage and its importance for system operation
Market Rules and Storage

## Slide 3
The Electrical System
Small and isolated without interconnection with other electrical systems

## Slide 4
Generation Unit Technology | Generating Station | Number | Installed Capacity (MW)
Conventional Units |  |  | 
Steam turbines | Vasilikos | 3 x 130 MW | 390.0
 | Dhekelia | 6 x 60 MW | 360.0
Combined Cycle Units | Vasilikos | 2 x 220 MW | 440.0
Gas turbines | Vasilikos, Moni | 5 x 37,5 MW | 187.5
ICE | Dhekelia | 6 x 16,7 MW | 100.2
 |  | Total (MW) | 1477.7
RES |  |  | 
Wind farms |  | 6 Wind farms (of which 5 are under the control and monitoring of the TSO) | 157.5
Photovoltaic systems |  | Connected to the Distribution System | 130
Biomass systems |  | Connected to the Distribution System | 9.7
 |  | Total (MW) | 297.2
 |  | TOTAL: | 1774.9
Generation 2019

## Slide 5
Percentage of Electricity Generation from RES 2017
Consumption
Target 2020 16%
Consumption 2017:
415.295 MWh 8,35%
RES share of total installed capacity: 15,9%

## Slide 6
Network Operation Issues
Network Operators have the responsibility to provide "ancillary services" for the regulation, economic and "good" operation of the system
  Frequency regulation
  Voltage regulation
  Inertia
  Power Quality
  Restoration after major disturbances
Important: Distributed Generation should be involved in providing ancillary services
TSO: Total responsibility for the security of the System
DSO: Responsibility of "good" distribution network operation - An important role in regulating voltages

## Slide 7
System Operating Challenges
Low load levels during the night and in the morning hours, especially during Spring & Autumn => problems with the minimum fixed loading of the reserved conventional Generation Units but also of the low inertia of the System

## Slide 8
Large and unexpected changes in wind power over a few minutes => demand for large amounts of spinning reserve
High Percent Ramp Rates of wind power affecting frequency regulation
System Operating Challenges

## Slide 9
System Voltage Control
Synchronous Generators
Capacitors
Inductors
SVCs
and other network elements
Generally, injection of reactive power into the system increases the voltages, and absorption of reactive power lowers voltage

## Slide 10
Ancillary Service Provision by RES
Stay connected to the grid in case of anomalies and cooperate with the central stations to avoid interruptions,
Reactive power support for voltage regulation,
Contribute to system stability, and
Smart metering and two-way consumer / producer communication with the network operator for observability and control of distributed generation, flexible demand and storage systems?

## Slide 11
The generating plants must be capable of reducing their active power at steps of maximally 10 % of the agreed active connection power. This power reduction must be possible in any operating condition and from any operating point to a target value given by the network operator. This target value is normally preset without steps or in steps, and corresponds to a percentage value related to the agreed active connection power. To date, target values of 100 % / 60 % / 30 % / 0 % are used.
RES Connection Rules Requirements by System Operator
Reduction of Active Power in relation to Frequency

## Slide 12
RES Connection Rules Requirements by System Operator
Power factor adjustment relative to output power
With active power output, it must be possible to operate the generating plant in any operating point with at least a reactive power output corresponding to a active factor at the network connection point of
cos ϕ = 0.9 under-excited to 0.9 over-excited
With active power output, either a fixed target value for reactive power provision or a target value variably adjustable by remote control (or other control technologies) are specified by the network operator in the transfer station.
The setting value is either
a fixed active factor cos ϕ or
an active factor cos ϕ (P) or
a fixed reactive power in MVar or
a reactive power/voltage characteristic Q(U).

## Slide 13
The minimum required wind farm capability for Reactive Power injection / absorption,
RES Connection Rules Requirements by System Operator

## Slide 14
Ancillary Service Provision by RES
Electrical storage facilities can provide important ancillary services

## Slide 15
Energy Storage Technologies
Advantages of LI-Ion Batteries:
  High energy density
  Low self-discharge rate
  No initial charging is required
  Low maintenance
LI-Ion Battery Disadvantages:
  Protection
  Aging
  Transport
  Cost (until recently)
  Developing technology
Notes: Lithium ion battery advantages:
High energy density: The much greater energy density is one of the chief advantages of a lithium ion battery or cell. With electronic equipment such as mobile phones needing to operate longer between charges while still consuming more power, there is always a need to batteries with a much higher energy density. In addition to this, there are many power applications from power tools to electric vehicles. The much higher power density offered by lithium ion batteries is a distinct advantage.
Self-discharge: One issue with batteries and ells is that they lose their charge over time. This self-discharge can be a major issue. One advantage of lithium ion cells is that their rate of self-discharge is much lower than that of other rechargeable cells such as Ni-Cad and NiMH forms.
No requirement for priming: Some rechargeable cells need to be primed when they receive their first charge. There is no requirement for this with lithium ion cells and batteries.
Low maintenance: One major lithium ion battery advantage is that they do not require and maintenance to ensure their performance. Ni-Cad cells required a periodic discharge to ensure that they did not exhibit the memory effect. As this does not affect lithium ion cells, this process or other similar maintenance procedures are not required.
Variety of types available: There are several types of lithium ion cell available. This advantage of lithium ion batteries can mean that the right technology can be used for the particular application needed. Some forms of lithium ion battery provide a high current density and are ideal for consumer mobile electronic equipment. Others are able to provide much higher current levels and are ideal for power tools and electric vehicles.
Lithium ion battery disadvantages:
Protection required: lithium ion cells and batteries are not as robust as some other rechargeable technologies. They require protection from being over charged and discharged too far. In addition to this, they need to have the current maintained within safe limits. Accordingly one lithium ion battery disadvantage is that they require protection circuitry incorporated to ensure they are kept within their safe operating limits. Fortunately with modern integrated circuit technology, this can be relatively easily incorporated into the battery, or within the equipment if the battery is not interchangeable.
Ageing : One of the major lithium ion battery disadvantages for consumer electronics is that lithium ion batteries suffer from ageing. Not only is this time or calendar dependent, but it is also dependent upon the number of charge discharge cycles that the battery has undergone. When a typical consumer lithium cobalt oxide, LCO battery or cell needs to be stored it should be partially charged - around 40% to 50% and kept in a cool storage area. Storage under these conditions will help increase the life.
Transportation: Another disadvantage of lithium ion batteries is that there can be certain restrictions placed on their transportation, especially by air. Although the batteries that could be taken in aircraft carry-on luggage are unlikely to be affected, care should be taken not to carry any more lithium ion batteries than are needed. Any carried separately must be protected against short circuits by protective covers, etc.
Cost: A major lithium ion battery disadvantage is their cost. Typically they are around 40% more costly to manufacture than Nickel cadmium cells. This is a major factor when considering their use in mass produced consumer items where any additional costs are a major issue.
Immature technology: Lithium ion battery technology is a developing area. This can be a disadvantage in terms of the fact that the technology does not remain constant. However as new lithium ion technologies are being developed all the time, it can also be an advantage as better solutions are coming available.
Superconducting magnetic energy storage (SMES)
Compressed air energy storage (CAES)

## Slide 16
Li-Ion Battery Storage
Battery power storage systems (BESS) are in the forefront of the latest era:
In 2017, ultra-modern battery projects have been announced and activated, such as the 120 MWh system in Escondido / Aliso Canyon, California, and Tesla's 100MW / 129MWh battery in Hornsdale, South Australia.
All these designs are made due to the price and scale that Li-ion technology has reached. Costs declined while production capacity increased very significantly. Storing battery power on a large scale is now a reality.
Worldwide installed power in 2017 was about 1 GW (with a share of Li-ion> 90%) and continues to go up exponentially.
The cost of the Li-Ion storage battery continues to fall:
Between 2010 and 2016, the industry-wide price has fallen by 73%, from $ 1,000 per kWh to $ 273 per kWh. By 2020, it is expected to fall to $ 145 per kWh and by 2025 to $ 69.5 per kWh.
52MWh Storage Battery - 13MW Photovoltaic Park on Kauai Island in Hawaii

## Slide 17
Energy Storage Facilities

## Slide 18
Energy Storage Applications

## Slide 19
Frequency Regulation
The energy storage system is charged or discharged in response to an increase or decrease, respectively of grid frequency.
This approach to frequency regulation is a particularly attractive option due to its rapid response time and emission-free operation

## Slide 20
Frequency Regulation

## Slide 21
Load levelling
Load leveling usually involves storing power during periods of light loading on the system and delivering it during periods of high demand. During these periods of high demand the energy storage system supplies power, reducing the load on less economical peak-generating facilities.
Postponement of investments in grid upgrades or in new generating capacity

## Slide 22
Load levelling

## Slide 23
Peak shaving
Peak shaving is similar to load leveling, but may be for the purpose of reducing peak demand rather than for economy of operation. The goal is to avoid the installation of capacity to supply the peaks of a highly variable load. Peak shaving installations are often owned by the electicity consumer, rather than by the utility.
Commercial and industrial customers save on their electricity bills by reducing peak demand.
Utilities reduce the operational cost of generating power during peak periods - reducing the need for peaking units.
Investment in infrastructure is delayed due to the flatter loads with smaller peaks

## Slide 24
Peak Shaving

## Slide 25
Capacity firming
The variable, intermittent power output from a renewable power plant, such as wind or solar, can be maintained at a committed (firm) level for a period of time.
The energy storage system smoothens the output and controls the ramp rate (MW/min) to eliminate rapid voltage and power swings on the electrical grid.

## Slide 26
Capacity firming

## Slide 27
Power quality
In power quality applications, an energy storage system helps protect downstream loads against short-duration events that affect the quality of power delivered.

## Slide 28
Power Quality

## Slide 29
To provide effective spinning reserve, the energy storage system is maintained at a level of charge ready to respond to a generation or transmission outage.
Spinning reserve
Depending on the application, the system can respond within milliseconds or minutes and supply power to maintain network continuity while the back-up generator is started and brought on line. This enables generators to work at optimum power output without the need to keep idle capacity for spinning reserves. It can also eliminate the need to have back-up generators running idle

## Slide 30
Spinning Reserve

## Slide 31
The Cyprus Energy Regulatory Authority (CERA) has put forward and published a proposal for the establishment of basic principles for the regulation of the operation of electricity storage upstream of the meter for public consultation purposes
Timetable:
The TSO will have to submit to CERA a final proposal for the amendment of the Transmission & Distribution Rules and the Market Rules for approval by 31 December 2019
Basic principles of the regulatory framework for the operation of electricity storage facilities in Cyprus

## Slide 32
Electricity storage facilities are divided into two basic categories depending on the point connected to the electrical system. Installations,
Upstream of the meter are the electricity storage facilities located on the side of the electricity system and before the consumer meter, they are not combined with on-site electricity consumption and their operation is planned and determined either by their participation in the Electricity Market or by the supply of services to the Transmission System and / or Distribution System.
Downstream of the meter are the electricity storage facilities on the consumption side and after the consumer meter. They are the installations where electricity consumption and storage coexist with or without on-site electricity generation
Basic principles of the regulatory framework for the operation of electricity storage facilities in Cyprus

## Slide 33
Two main comments on the proposed operating framework are:
Provision of services to the grid from electricity storage facilities only upstream of the meter,
Entities providing regulated electricity transmission and / or distribution services such as the TSO and the DSO may not own electricity storage facilities upstream of the meter due to the commercial nature of these services.
Basic principles of the regulatory framework for the operation of electricity storage facilities in Cyprus

## Slide 34
The full development and penetration of microgids and RES technologies into the system requires the large-scale use of energy storage technologies, especially in small and isolated networks,
Legislation should help to the fullest extent of promoting storage technologies at all levels of the network.
Conclusions

## Slide 35: Thank you for your attention
Dinos Charalambides
Electrical Engineering Consultant
7, Nikitara Street
2321 Lakatamia
Nicosia
Tel: +357 99 664861
Email: dinos.charalambides@gmail.com
Acknowledgment